# DCGen Web Datacenter Configuration Platform — User Manual

Version 1.0 ｜ 2026-08-17 ｜ English edition ｜ Applies to: Kimi hosted deployment and GitHub self-hosted version (pcpcchen-coder/AIDCalculator)

## Chapter 1　About This System

### 1.1 What is this?

DCGen Web is a datacenter hardware configuration generation platform built on the DCGen 1.1 technical report (arXiv:2604.09616, University of Chicago / Argonne National Laboratory) and its open-source implementation. Enter the datacenter type and scale target, and the system automatically computes:

- IT configuration: how many racks each node type (GPU, CPU-GPU, CPU, Storage) requires, peak power in MW, power density (kW/m²), and how much White space (IT floor space in m²) is needed.

- Cooling system: how many CDUs, chillers, and dry coolers / cooling towers are required, which commercial model is selected, and how much power they consume.

- Power distribution system: how many PDUs, UPSs, MSBs (main switchboards), and backup generators are required (including N+1 / 2N / xN-y redundancy and safety margin), and the conversion losses.

- Gray space: floor space occupied by cooling and power distribution infrastructure (indoor / outdoor m²).

### 1.2 What the system can do (by page)

| Need | Where to do it |
| --- | --- |
| Generate a datacenter configuration and view result charts | Generator /generator |
| Save scenarios, reopen them later, compare multiple scenarios side by side | “Saved Scenarios” at the bottom of the Generator |
| Browse / add / edit / delete equipment catalogs (including Delta Electronics products) or IT reference configurations | Database Management /catalog |
| Tune model parameters (e.g., the safety margin default), add your own parameters | Parameters /parameters |
| View paper Eq. 1–19 algorithms, adjust algorithms, add your own algorithm formulas and evaluate them | Algorithms /algorithms |
| Learn about the DCGen model, redundancy vocabulary, and data sources | Model Docs /docs |

### 1.3 Three-minute glossary

| Term | Plain explanation |
| --- | --- |
| White space | Floor space for IT racks (m²) |
| Gray space | Floor space for cooling and power distribution facilities (split into indoor/outdoor) |
| Power density | How many kW per square meter (measures how much power fits in the same space) |
| Canonical configuration | The paper’s “standard configuration” obtained by averaging multiple real systems (three eras: 2024/2027/2029) |
| Reference configuration | Real systems (e.g., xAI COLOSSUS, DGX SuperPOD, Aurora) |
| Redundancy N+1 / 2N / xN-y | If N units are needed, keep r extra; 2N = two full sets; xN-y = each unit delivers only y/x of its capacity |
| Safety margin (sm) | Additional over-provisioning ratio for equipment (0.2 = 20% more) |
| pod | Rack group unit = rows_per_pod × rack_per_row (default 2×10 = 20 racks/pod); CDUs/PDUs are provisioned per pod |
| engineEligible | Catalog switch: whether the equipment participates in automatic selection |

## Chapter 2　Five-Minute Quick Start

Goal: generate your first configuration — a 1,000-rack AI training datacenter.

- Open the website and click “Generator” in the left sidebar.

- The form defaults are basically fine:

  - Datacenter type: AI Training

  - Target: Rack count 1000

  - Model: Canonical, year 2024

  - Heat rejection mode: Dry cooling; optimization criteria: check both Space and Power

  - Redundancy: defaults (cooling side N+1, power side 2N); safety margin 20%

- Click “Generate”. Results will appear on the dashboard to the right.

- Check against expected results (these numbers have been verified item-by-item against the original Python DCGen):

  - IT peak power ≈ 143.6 MW (GPU 888 racks / 140.3 MW + Storage 112 racks / 3.3 MW)

  - Power density ≈ 79.8 kW/m²; White space = 1,800 m²; 50 pods in total

  - Power optimization: dry cooler Vertiv Liebert *D**112 × 4,983 units, chiller × 385, CDU CoolIT CHx2000 × 150 (3 per pod); cooling power ≈ 26.6 MW

  - UPS (IT phase) = Delta Modulon DPH-G3-1250K × 276 units (note: Delta products are marked with a green dot in the BOM table)

- Click “Save Scenario” in the upper right → name it (e.g., “AI Training 1000 racks 2024”) → you can reopen it or use it for comparison anytime later.

If the numbers don’t match: go to “Parameters” and click “Restore all defaults”, then try again (you may have changed global parameters).

## Chapter 3　Interface Overview

### 3.1 Layout structure

- Left sidebar (240px): six page links + version badge + paper/REPO external links; on mobile it becomes a top-bar hamburger menu.

- Page header (top of each page): breadcrumb, page title, one-line description, and the primary action button on the right (e.g., “Add Data”, “Generate”).

- Main content area: the functional area of each page.

### 3.2 Common component semantics

| Component | Usage |
| --- | --- |
| Table | Click a column header to sort; click a row to expand details; hover to reveal more actions |
| Badge | Category colors: cyan = Canonical/built-in, violet = Reference/custom, amber = modified/warning, green = Delta Electronics/success |
| Right-side drawer | Form for adding/editing an entity; closes via the ✕ in the upper right or after submission |
| Confirmation dialog | Always asks “Confirm deletion?” before deleting; red button confirms |
| Toast (appears in upper right) | Green border = success, red border = failure (backend error message attached), auto-dismisses after 4 seconds |
| Empty state | Rack line-art illustration + guidance button (e.g., before any result has been generated) |

### 3.3 Numeric display conventions

- Power: MW primarily (individual equipment in kW); space: m²; power density: kW/m².

- “—” means the manufacturer has not published that value (e.g., total power draw of some CDUs); the system does not fabricate numbers. Such equipment ranks below fully documented items in the corresponding efficiency comparisons.

## Chapter 4　Generator: Complete Guide

### 4.1 Form fields, item by item

A. Basic requirements

| Field | Description | Example / note |
| --- | --- | --- |
| Datacenter type | AI Training / AI Inference / Mixed AI Training & Inference / Cloud | Determines the node type mix (training = GPU+Storage; inference = CPU-GPU+CPU+Storage; mixed = GPU+CPU-GPU+Storage; cloud = CPU+Storage) |
| Target mode | “Rack count” or “Power” | Rack count = directly specify the total rack count (e.g., 10000); Power = enter a string such as 100MW or 1GW (the system back-computes the rack count) |
| Model | Canonical / Reference | Canonical = paper standard configuration; Reference = real systems |
| Year (Canonical) | 2024 / 2027 / 2029 / All | 2027/2029 are high-density projections (GPU racks at 600kW/1000kW); selecting All produces one result for each of the three eras |
| Reference configurations (Reference) | Multi-select checklist | None checked = one result for every system; checked = compute only the selected ones |
| Optimization criteria | Space / Power (at least one) | Check both → two sets of equipment selections shown side by side, switchable for comparison |

B. Cooling

| Field | Description |
| --- | --- |
| Heat rejection mode | Dry cooling (Dry cooler; water-saving, large outdoor footprint) / Evaporative cooling (cooling tower; better energy efficiency) |

C. Redundancy (seven slots)

Each slot can be set to N, N+1, N+2, 2N, or a custom xN/y (e.g., 3N/2). When xN/y is selected, the interface immediately shows “Deliverable capacity = y/x × rated”. The seven slots: heat rejection, chiller, CDU, PDU, UPS, MSB, backup generator. Defaults: all cooling-side slots N+1, all power-side slots 2N.

D. Advanced (collapsed by default)

| Field | Description | Default |
| --- | --- | --- |
| Safety margin | Equipment over-provisioning ratio slider (0–100%) | 20% (from the global parameter safety_margin) |
| rack_per_row | Racks per row | 10 |
| rows_per_pod | Rows per pod | 2 |

The defaults of these three fields come from the global parameters in “Parameters”. Changing them in the form affects only the current calculation; changing them in Parameters changes the defaults.

### 4.2 Example 1: 10,000-rack AI training center (2024)

Input: AI Training ｜ rack count 10000 ｜ Canonical 2024 ｜ everything else default.

Expected results (verification baseline):

| Metric | Value |
| --- | --- |
| GPU racks | 8,876 racks / 1,402.4 MW |
| Storage racks | 1,124 racks / 33.4 MW |
| Total IT power | 1,435.8 MW (≈1.4GW) |
| Power density | 79.77 kW/m² |
| White space | 18,000 m² |

### 4.3 Example 2: 1GW power target

Input: AI Training ｜ switch target to “Power” and enter 1GW ｜ Canonical 2024.

Expected results: total racks 6,965 (GPU 6,182 + Storage 783), White space ≈ 12,537 m². The logic of power-target mode: first compute the reference configuration’s power density, then back-compute with rack count = target power ÷ (density × floor space per rack).

### 4.4 Example 3: 2027 high-density projection

Input: AI Training ｜ rack count 10000 ｜ Canonical 2027.

Expected results: GPU racks become 600 kW/rack, total IT power jumps to ≈ 3.3 GW, power density ≈ 183 kW/m² — for the same ten thousand racks, 2027 power is 2.3× that of 2024 (one of the paper’s core findings). Switching to 2029 shows ≈ 4.7 GW. Recommended: use “All” to generate all three eras at once, then compare scenarios (see Chapter 6).

### 4.5 Example 4: Using a real system as reference (Reference mode)

Input: AI Training ｜ rack count 2000 ｜ switch model to Reference ｜ check “xAI COLOSSUS” in the reference configuration list.

The system scales COLOSSUS’s ratios (GPU:Storage = 1563:203, GPU 100kW/rack 48U normalized to 42U) to 2,000 racks and computes the corresponding cooling and power distribution. If nothing is checked, one result is produced for each reference system in the list (good for comparing different real-world designs side by side).

### 4.6 Example 5: Dry cooling vs evaporative cooling

Run the same input twice (once dry, once evaporative), save each as a scenario, then compare:

- Dry: the heat rejection side needs many dry coolers (e.g., 4,983 small units or 628 large units), large outdoor footprint (over ten thousand m²), but low water use.

- Evaporative: fewer cooling towers (tens of units), high energy efficiency (low share of cooling power), suitable where water is plentiful.

When comparing, just look at “Gray space outdoor” and “cooling power” to see the trade-off.

### 4.7 Example 6: Impact of N+1 vs 2N

Change the UPS slot from 2N to N+1 and regenerate: the UPS count drops noticeably (e.g., from 276 units to about half), but fault tolerance also drops. 2N’s “deliverable capacity = 1/2 × rated” is the key — for the same capacity requirement you buy twice the equipment. Try a custom xN/y of 3N/2: each unit delivers only 2/3, and the count lands between the two.

## Chapter 5　Reading the Results Dashboard

After generation, the right side shows, in order:

- Four metric cards: total rack count (with per-node-type breakdown), IT peak MW (with IT + cooling + losses breakdown), power density, White space (with Gray indoor/outdoor hint).

- Configuration / criterion switcher: when multiple configurations or optimization criteria exist, use the Segmented control on top to switch (Space / Power).

- Power composition stacked bar: IT vs cooling power vs power distribution losses (including the safety margin segment); hover over the legend for percentages.

- Dual donuts: space distribution (White vs Gray indoor vs Gray outdoor) and rack distribution (by nodeType).

- Gray space metric tiles: indoor / outdoor m².

- Cooling BOM table: the selected equipment in each category — model, vendor (Delta = green dot), quantity, units per pod (row-level equipment), total capacity MW, power draw MW, space m². Hover over a model to see “View in catalog”.

- Power distribution BOM table: split into “IT phase” (supporting the IT load) and “facility phase” (UPS/MSB/Gen supporting cooling power), with efficiency and conversion loss MW.

- Parameter snapshot (collapsible): all global parameter values used in this calculation (those differing from defaults marked in cyan), with one-click JSON copy — attach it when citing in a paper or report so others can reproduce your results.

If the form was changed but not re-run, the dashboard shows an amber “parameters changed” badge to remind you the results are stale.

## Chapter 6　Scenario Management: Save, Reopen, Compare

### 6.1 Saving and reopening

- After generating results, click “Save Scenario” → name it (the system pre-fills “type + scale + year”) → saved to the database.

- The “Saved Scenarios” list at the bottom of the page: searchable, filterable by type; “Open” back-fills the scenario’s inputs into the form and re-displays its results; “Copy parameters” quickly applies them; “Delete” requires confirmation.

### 6.2 Scenario comparison (up to 3)

Check 2–3 scenarios → click “Compare Selected” → a bottom drawer expands with a comparison table:

- One metric per row (IT MW, density, White/Gray space, equipment counts per category), one scenario per column, maximum value highlighted in cyan.

- Includes dual grouped bar charts of peak power and space; the comparison can be exported as CSV.

Example workflow (era evolution analysis): using the method from Example 4.4, save 2024, 2027, and 2029 as three scenarios with Canonical “All” → select all and compare → you get a complete comparison table of “same 10,000 racks, power 1.4GW → 3.3GW → 4.7GW”, ready to export as CSV for charting.

## Chapter 7　Database Management (/catalog)

### 7.1 Browsing the equipment catalog

- Eight category pills at the top (CDU / chiller / dry cooler / cooling tower / PDU / UPS / MSB / backup generator, with count badges).

- Vendor multi-select dropdown, search box (model or vendor, 300ms debounce).

- “Delta only” green switch: shows only Delta’s 20 products (Delta rows have a left green bar + brand badge). Visiting /catalog?vendor=Delta directly also enables it automatically.

- Click a row to expand three-column details: full specifications / dimension proportion bar / full source text + “Generate configuration with this equipment →”.

- Each equipment entry includes a source URL (external-link icon) for tracing back to the manufacturer’s catalog.

### 7.2 Adding equipment (example: adding an in-house CDU)

- Click “＋ Add Data” in the page header (on the “Equipment Catalog” tab) → the right-side drawer opens.

- Fill in:

  - Name: ACME LiquidCDU 2500, vendor: ACME (a new vendor is created automatically if it doesn’t exist)

  - Category: CDU (Coolant Distribution Unit) → the form automatically shows the “Peak power draw (kW)” field (power-distribution categories show “Efficiency (0-1)” instead)

  - Capacity: 2500 kW, peak power draw: 15 kW

  - Dimensions H/W/D: 2.2 / 1.1 / 1.3 m (proportion bar shown live), λ maintenance aisle ratio: 0.2

  - Year: 2026, source URL: https://example.com/datasheet

  - engineEligible: on (so the engine can select it)

- Save → success toast → the new row flashes cyan. From then on, this unit competes in CDU selection whenever a configuration is generated.

Validation rules: capacity must be > 0; efficiency 0–1; year 1950–2035; URL must be valid. Errors are indicated with a red border.

### 7.3 Editing and engineEligible

- Click “Edit” on a row → modify values in the same drawer. Common uses: fill in measured values for equipment whose manufacturer omitted power draw, or turn a device’s engineEligible off (kept in the catalog but not selected by the engine).

- In the seed data, “rack-level rPDU / small power cabinet” defaults to engineEligible = off (they are not pod-level equipment); you can turn them on manually when needed.

### 7.4 IT configuration management (example: creating your own reference configuration)

Switch to the “IT Configurations” tab → “＋ Add Data”:

- Name: My Lab Cluster, type: AI Training, model: Reference

- RackSize: 48, RackType: Cloud, floorSpace: 2.0, Generation: 2026

- nodeTypes dynamic rows: GPU × 20 racks × 80 kW + (click “Add node”) Storage × 3 racks × 25 kW; the bottom live-displays “total racks 23 · total IT power 1,675 kW”

After saving, choosing Reference mode in the Generator lets you check “My Lab Cluster” as a ratio template. Each card also has “Duplicate” (quickly create a variant) and “Generate with this configuration →”.

### 7.5 Export

The “Export” dropdown in the page header: downloads the currently filtered results (including category/vendor/search conditions) as JSON or CSV; the toast shows the record count.

## Chapter 8　Parameters (/parameters)

### 8.1 Interface

Left-side category navigation (scroll-spy): Architecture & Design / IT Model / Storage Estimation / Custom Parameters. Each row shows the key (monospace), current value, default value, unit, and description.

### 8.2 Example: adjusting the safety margin

- Find safety_margin (default 0.2) → click the value for inline editing (or drag the slider) → change to 0.3 → Enter.

- An amber “modified” badge appears on that row; a new entry (0.2 → 0.3) is added to the “Change History” panel on the right.

- Effect: the form’s safety margin default becomes 30% in subsequent generations, and the (1+sm) factor in all equipment counts scales up — e.g., a UPS count goes from 276 units to 300.

- Click ⟲ to restore a single entry to its default; “Restore all defaults” in the page header restores them one by one (confirmation required).

### 8.3 Example: adding a custom parameter

- “Add Custom Parameter” → drawer: enter key custom_pue_target (the system automatically adds the custom_ prefix; alphanumeric and underscore only, duplicates flagged immediately).

- Value 1.25, unit ratio, category defaults to “Custom Parameters”, description “Target PUE (for custom algorithms)” → Create.

- Use: when writing custom formulas in “Algorithms” you can directly reference custom_pue_target (its value is auto-filled during evaluation); custom parameters can be deleted, built-in parameters cannot (they can only be adjusted or restored).

### 8.4 Change history

The panel shows the most recent 50 entries: action badge (update/create/reset/delete), old value → new value, timestamp. Modifications not yet restored in the current session are grouped at the top and can be restored row by row.

## Chapter 9　Algorithms (/algorithms)

### 9.1 Navigating the registry

15 built-in algorithms (corresponding to paper Eq. 1–19 and architectural methods), grouped by category: Storage Estimation (3), IT Model (5), Redundancy (1), Cooling & Power Equipment (3), Architecture & Design (3). Select one in the left list; the right side shows: equation number (e.g., Eq. (2)(5)), version, formula card (color-coded variables), description, enabled switch, and parameter bindings.

### 9.2 Adjusting built-in algorithms

- Editable: description, parameter bindings (formula variables ↔ global parameter keys), enabled, category; after saving, the version number auto-increments by +0.1 (e.g., 1.0 → 1.1, and a “modified” badge appears in the list).

- Not editable: built-in core formulas (to protect model correctness). To change a formula → use “Duplicate as Custom” to create an editable copy.

### 9.3 Evaluation panel (example)

Select “Storage rack estimation (power proportion method)” → the evaluation panel lists the variables (p, computeRacks, computeTdpKw, rackSize, nodeTdpKw) → global parameters with matching names are auto-filled; fill in the rest manually:

- p = 0.042, computeRacks = 300, computeTdpKw = 158, rackSize = 42, nodeTdpKw = 0.708

- Click “Compute” → result 70 (⌈0.042×300×158 ÷ (0.958×42×0.708)⌉), with the substitution steps shown line by line below.

### 9.4 Complete custom algorithm examples

Example A: total power draw estimation with PUE

- “Add Custom Algorithm” → drawer:

  - key: custom_total_power_with_pue, name: Total power estimation with PUE, category: Custom Algorithms

  - Formula: itPowerMw * custom_pue_target (first create custom_pue_target = 1.25 in Parameters)

  - The editor performs live syntax checking (✓ green / ✕ red + a list of available variables); you can also click “Insert parameter” to insert a global parameter at the cursor.

- After saving, go to the evaluation panel: itPowerMw = 1000 → custom_pue_target = 1.25 is auto-filled → result 1250 MW.

Example B: improved storage estimation (change the proportion to 6%)

- On the built-in storage_from_power_proportion, click “Duplicate as Custom” → enter newKey custom_storage_6pct.

- Edit the copy’s formula to: ceil(0.06 * computeRacks * computeTdpKw / ((1 - 0.06) * rackSize * nodeTdpKw)) (it must pass validation before saving).

- Evaluate with computeRacks=300, computeTdpKw=158, rackSize=42, nodeTdpKw=0.708 → 100.

Formula support: + - * / % ^, parentheses, functions ceil floor round sqrt abs min max log log10 exp pow sum. Formulas are not executed via eval; they are evaluated by a whitelist parser, so there is no injection risk.

## Chapter 10　Hands-On Workflows

### Workflow 1: Planning a 100MW AI inference center

- Generator: AI Inference ｜ power 100MW ｜ Canonical 2024 ｜ dry cooling ｜ check both optimization criteria.

- Review results: rack count (on the order of ~29,000 racks), CPU-GPU/CPU/Storage distribution, and switch between the Space and Power equipment selections to compare.

- Save scenario “100MW inference - dry”; change heat rejection to evaporative cooling, run again, and save “100MW inference - evaporative”.

- Compare the two scenarios: outdoor Gray space (much larger for dry) vs cooling power (lower for evaporative) → write into your evaluation report.

### Workflow 2: Evaluating the role of Delta equipment in a new design

- In the catalog, turn on “Delta only” and check the specs of GoCool-1500 (1.5MW CDU, GB200 NVL72 certified) and the DPH-G3-1250K UPS.

- Generate a high-density configuration (e.g., Canonical 2027).

- Check the BOM: if a Delta CDU wins in the cooling category it shows a green dot; see the winning UPS models and counts in the IT/facility phases.

- To force adoption of a specific Delta model: temporarily turn off competitors’ engineEligible and regenerate (or edit competitors’ capacity/efficiency in the catalog for what-if analysis).

### Workflow 3: 2029 ultra-high density (1MW/rack) feasibility study

- AI Training ｜ rack count 5000 ｜ Canonical 2029 ｜ check both optimization criteria.

- Observe: IT reaches several GW, Gray space may reach 4–6× White space — exactly the finding of paper §5.2.

- Combine with redundancy adjustments (e.g., heat rejection N+2) to evaluate the space cost; save three scenarios, compare them, and export CSV as evidence.

### Workflow 4: Plugging your own estimation model into the platform

- In Parameters, add custom_storage_ratio = 0.06.

- In Algorithms, add a formula (referencing custom_storage_ratio) and validate it with the evaluation panel.

- Back in the Generator, run the built-in model with the same inputs and compare against your estimate — the platform becomes your model validation tool.

## Chapter 11　FAQ & Troubleshooting

| Problem | Solution |
| --- | --- |
| Clicking “Generate” shows “No matching IT configuration found” | Check the type/model/year combination (Reference’s “Mixed AI Training & Inference” itself has no reference system; use Canonical instead) |
| A device in the BOM table shows “—” for power draw | The manufacturer has not published that value (the catalog notes explain); you can edit the catalog entry to add a measured value |
| Result numbers differ from this manual | You changed values in Parameters — “Restore all defaults” and re-run |
| Catalog changed but results didn’t | Confirm the equipment’s engineEligible is on; and it only wins if its efficiency/space efficiency truly beats others in the same category |
| Custom formula won’t save | Syntax check failed (red ✕) — fix per the hints; variable names may use only alphanumeric characters and underscores |
| Want to change a built-in algorithm’s formula | Built-in formulas are locked; use “Duplicate as Custom” and edit the copy |
| Failed to delete a built-in parameter/algorithm | Built-in items can only be adjusted or disabled, not deleted |
| Power string format error | Supports number+W/kW/MW/GW/TW (e.g., 500kW, 1GW); must be positive |
| Can others see my changes? | The hosted deployment shares one database among all visitors; changes are shared instantly (currently no login mechanism) |
| Will data disappear after an update? | Kimi full-stack version: no (data lives in the cloud DB; new versions do not wipe it); self-hosted version: in your own MySQL |
| How to reproduce someone else’s results? | Ask them for the scenario’s “parameter snapshot” JSON, align values one by one in Parameters, then re-run |

## Chapter 12　Glossary

| Term | English | Description |
| --- | --- | --- |
| Rack TDP | Rack TDP | Peak power draw of a single rack (kW/rack) |
| Node type | Node type | GPU / CPU-GPU / CPU / Storage |
| Conventional rack | Conventional rack | 42U (EIA-310); other sizes are normalized |
| HPC rack | HPC rack | Supercomputing cabinet; power converts to Cloud racks at × 2/3 |
| Row-level equipment | Row-level | CDU, PDU (provisioned per pod) |
| DC-level equipment | DC-level | Chiller, heat rejection, UPS, MSB, generator |
| Facility phase | Facility phase | The second layer of UPS/MSB/Gen design supporting “cooling power” |
| Optimization criterion | Optimization criterion | Space (kW/m² priority) or Power (efficiency priority) |
| Deliverable capacity | Deliverable capacity | Under xN/y, each unit delivers only y/x × rated |
| Parameter snapshot | Parameter snapshot | All global parameter values at the moment of calculation, for reproducibility |

## Appendix A　Expected Results Quick Reference (verification baseline)

The following baseline values have been verified item-by-item against the original Python DCGen under the same catalog (36/36 match) and can serve as a sanity check while you work:

| Scenario | Key results |
| --- | --- |
| AI Training 2024, 10,000 racks | Density 79.766 kW/m²; IT 1,435.791 MW; GPU 8,876 racks; White space 18,000 m² |
| AI Training 2024, 1GW | Total racks 6,965 (GPU 6,182 + Storage 783); White space 12,536.9 m² |
| Cloud 2024, 10,000 racks | IT 186.459 MW; density 10.359 kW/m² |
| AI Training 2024, 1,000 racks (dry cooling, sm 0.2, cooling N+1, power 2N) | 50 pods; Power optimization: dry cooler ×4,983, chiller ×385, CDU ×150, PDU ×500, UPS ×276(IT)+52(facility), MSB ×30+6, generator ×36+8; cooling power 26.571 MW |

## Appendix B　Built-in Algorithms (15)

| key | Name | Equation |
| --- | --- | --- |
| storage_from_capacity | Storage rack estimation (capacity method) | Eq. (1) |
| storage_from_power_proportion | Storage rack estimation (power proportion method) | Eq. (2)(5) |
| storage_from_iops | Storage rack estimation (IOPS method) | Eq. (3) |
| it_rack_distribution | IT rack distribution scaling | Eq. (7a)(15a) |
| it_peak_power | IT peak power | Eq. (8) |
| it_power_density | Power density | Eq. (9)(12) |
| it_floor_space | IT floor space (White space) | Eq. (10)(13) |
| rack_count_from_power | Rack count back-computed from power target | Eq. (14) |
| rack_tdp_normalization | Rack size normalization | Eq. (11) |
| npr_pod_hardware | N+r row-level equipment count | Eq. (16a)(16b) |
| npr_dc_hardware | N+r DC-level equipment count | Eq. (17a)(17b) |
| xny_effective_capacity | xN/y deliverable capacity | Eq. (18a) |
| xny_hardware_count | xN/y equipment count | Eq. (18b-c)(19a-b) |
| gray_space | Gray space estimation | Eq. (17c)(19c) |
| lpt_pod_packing | LPT rack pod packing | §4.6.1 |

The system described in this manual is a research prototype; equipment specifications are taken from each vendor’s official catalog (see the data source statement on the system’s “Model Docs” page) and are for research use only. For the original DCGen model, please cite: Gnibga, W. E., & Chien, A. A. (2026). DCGen 1.1 Technical Report. arXiv:2604.09616.